## Slide 1
48V Power Shelf Operation
Author: Ed Fontana
Author: Paul Smith
Author: Mark Johnson
GE Industrial Solutions

## Slide 2: Background
Motivation:
Running at full power down to 42 Volts requires higher output currents from each rectifier. High current causes component stress in the DC/DC converter part of the power supply. These stresses include i^2*R losses in the magnetics and ripple current in the filtering capacitors. Accommodating these stresses increases cost and size, and through use of a coordinating specification (Open Rack 2.0) is unnecessary.

## Slide 3: Cost avoidance options
Coordination of loads to support a full power requirement over a range from +48V to +59.5V (roughly +/- 10% range around the +54V operating point) could be done with the use of turn on hysteresis with a turn on threshold of 48V. This would cause no change to the operational range of the loads: +40 to +59.5V for the IT loads and +38 to +59.5V for the battery modules.
The turn on hysteresis value of 48V need only apply to 80% of the full load value for each system element. It does not apply to control and communication functions of the loads.

## Slide 4: DC Output Characteristics with Batteries – historical values
54.5V DC Voltage – typical legacy value associated with float charging of VRLA batteries
42.0V DC – typical End of Discharge (EoD) voltage for non destructive use of VRLA batteries
Not necessarily optimum for Lithium Ion or other chemistries

## Slide 5: Spec Changes
In Appendix A - 48V Rectifier Specification with Single Phase AC input
A.2.3.11 DC Output
The DC output voltage of the rectifier shall be configurable from 42V to 58V (settable via SW), while in operation. The default
set point shall be 54.5 V DC (factory default). The rectifier shall supply rated power for the entire range of DC output voltage of 48V to 58V. For the 42-48V range, the rectifier shall supply full power at 40C ambient temperature and can be derated by
maximum 87.5% at higher temperatures.

## Slide 6: Spec Changes
In Appendix B - 48V Battery Unit Spec
B.2.2 Input / Output
B.2.2.1 Vin
This terminal is at a positive potential when voltage is measured with respect to return. Vin pin connects to the shared bus
voltage. Battery unit shall be enabled over the Vin voltage range of 38V to 59.5V.
After a power interruption, or upon cold start, the IT load must provide turn on hysteresis such that 80% of the load does not turn on until the rack system bus voltage reaches + 48Vdc.

## Slide 7: Spec Changes
In section 6.0 48V IT Tray Power Spec:
6.2 Input Voltage level
Nominal level: +54.5V DC
Range: +40V to +59.5V DC
The (rack) system uses an always-on power supply with voltage delivered over a common bus bar that provides a fixed voltage to payloads in the range +40V to +59.5V. All payload voltage regulators must be designed to support this input voltage range.
After a power interruption, or upon cold start, the IT load must provide turn on hysteresis such that 80% of the load does not turn on until the rack system bus voltage reaches + 48Vdc.